## Slide 1: Bottom-up Vulnerability Analysis Preliminary results & discussion
Jacob Everitt
David E. Rosenberg
February 28th, 2020
Weber Basin Water Conservancy District

## Slide 2
Key Steps
1. Identify factors
2. Develop scenarios
3. Run Riverware / Riversmart
4. Define vulnerability criteria (Fraction of years …)
5. Visualize vulnerabilities
6. Discuss
Contour plots
Time series
Total storage ≤ Yellow, Orange, Red targets
Shortages > 0
216 Runs
(Scenario combinations)
Flow @ Oakley
Paleo
Observed
Future Climate
Six 30-yr blocks (800 - 970 kaf/yr)
Demand
Per capita use (6)
Population (3)
Decreased Ag. (3)
Potential ET (7)
6 scenarios
(380 - 850 kaf/yr)
Sediment Buildup
None
1 or 2 events
Gradual
3 scenarios
(0%, 10%, 30%)
Evaporation Rate @ Willard Bay
Riverware
Historical
Late estimate
3 scenarios
(3.2, 3.7, 4.0 ft/yr)

## Slide 3
Project examples
Flows
Demands
Sedimentation
Evaporation
Adapted from Wang et. al. (2020)
Scenarios express deep uncertainty about future conditions
Certain
Ignorance
Deep Uncertainty

## Slide 4
1570-1600
1520-1550
1930-1960
1940-1970
Hot Dry
1610-1640
Weber River Flow at Oakley
(acre-feet per year)
Selected 6 flow scenarios

## Slide 5
Location | Flow Range (kaf per year)
Weber @ Oakley | 94 to 120
Total basin (RiverWare) | 800 to 970
Context for flow scenarios
56 kaf (Mod. emiss., low precip.)
163 kaf (Mod. emiss., med. precip.)
130 kaf (High. emiss., med. precip.)
39 kaf (High. emiss., low precip.)
U of U
UCRFC Estimates
98 to 202 kaf
We do not use very high flow scenarios!!
Weber River Flow at Oakley
(acre-feet per year)
Water Year
U of U LOCO Estimates

## Slide 6
3 demographic and 1 climate factors effect demand
Base Case
Demand
(acre-feet per year)
Notes: https://rpubs.com/Jeveritt/578647

## Slide 7
Selected 6 of 63 demand scenarios

## Slide 8
A bit more on …
Scenario | Decrease in total storage | Comment
None | 0% | Current assumption
Single debris event | 1.4% | e.g. Fill Causey. Not modeled.
Gradual over time | 10% | Echo, Wanship, East Canyon 0.1 to 0.2% per year (UDWR 2010) Assume all loss at model beginning
Extreme | 30% | Purposefully higher than observed
Scenario | Rate (ft/yr) | Comment
RiverWare | 3.2 | Current model value
Historical | 3.7 | 1995 to 2005 (U of U, 2019); 1,500 ac-ft/yr
Late 21st Century | 4.0 | 2085 to 2095 (U of U, 2019); 3,300 ac-ft/yr
Reservoir Sediment Buildup
Evaporation Rate @ Willard Bay

## Slide 9
Current ok. Storage vulnerable to 100k acre-feet per year changes in inflow or demand
36 inflow-demand combos
Percent of June 1 system storage values below 380,000 acre-feet
Sedimentation = 0%
Willard Bay evap. = 3.2 feet/year

## Slide 10
108 inflow-demand-sediment combos
Percent of 30 years system storage below moderate, severe, extreme levels
Willard Bay evap. = 3.2 feet/year
Storage mildly sensitive to 10% storage loss; At 30% sedimentation, storage more sensitive to inflows than demand
Notes: 1610 to 1640 inflow effects the Storage (Has duration droughts)
1570 to 1600 inflow effects the Storage (Has high intensity droughts)

## Slide 11
Willard Bay evap. = 3.2 feet/year
Long & severe droughts drop reservoir storage below 280,000 acre-feet even with 0% sedimentation
Larger demands
Lower flow

## Slide 12
Willard Bay evap. = 3.2 feet/year
Monthly shortages insensitive to reservoir sedimentation
Larger demands
Lower flow

## Slide 13
Willard Bay evap. = 3.2 feet/year
Largest shortages coincide with low storage and inflows (expected)
Larger demands
Lower flow

## Slide 14
Percent of years Riverware shortage > DCP shortage
Riverware model shorts users more than Drought Contingency Plan across all tested inflow & demand scenarios
Sedimentation = 0%
Willard Bay evap. = 3.2 feet/year

## Slide 15: We are still working on evaporation
Riverware results identical for each evap. scenario
UofU suggested 1,600 to 3,300 acre-feet/year increases for 3.7 and 4.0 feet/year (assume full pool of 9,970 acre-feet).
When we multiply area by rates:
  ~ 30,000 acre-feet per year total evap.
  ~ +6,600 to +8,000 acre-feet/year additional over 3.2 feet/year rate
4. Evap. will decrease as reservoir storage drops (e.g., many scenarios)
5. 8,000 acre-feet is real water, but maybe noise for a vulnerability study?

## Slide 16: Summary of System Vulnerabilities
Inflows and Demands
  Currently okay
  Start to hit moderate storage target with changes of ~100k acre-feet per year
Sedimentation
  Storage mildly sensitive to 10% reservoir volume loss
  Shortages insensitive to sedimentation
Willard Bay Evaporation
  System storage insensitive over 3.2 to 4.0 feet per year range tested
Factor Combinations
  Long & severe droughts drop reservoir storage below 280,000 acre-feet even with no sedimentation
  Largest shortages coincide with lower storage and inflows (expected)
  Storage more sensitive to inflow than demand changes at largest sedimentation rates
  Riverware shorts users more than DCP across tested inflow and demand scenarios. Increase DCP shortages, esp. for moderate tier?

## Slide 17: Our Next Steps
Get evaporation results to work
Relate demand scenario values back to multiple sub-factors
Look at Willard Bay storage individually
Relate average and max annual shortages
Draft report/thesis
Jacob defend thesis
Final report

## Slide 18: Discussion Points
What do you like?
What is new for you? What could change how you will manage?
What should we clarify/add/change for draft & final reports?
Percent of June 1 system storage values below 380,000 acre-feet​